HD 60364-4-41:2007:

411.4.4 The characteristics of the protective devices (see 411.4.5) and the circuit impedances shall fulfil the following requirement:

Zs ( Ia Uo

where

Zs 
is the impedance in ohms (() of the fault loop comprising 

–
the source, 

–
the line conductor up to the point of the fault, and 

–
the protective conductor between the point of the fault and the source;

Ia 
is the current in amperes (A) causing the automatic operation of the disconnecting device within the time specified in 411.3.2.2 or 411.3.2.3. When a residual current protective device (RCD) is used this current is the residual operating current providing disconnection in the time specified in 411.3.2.2 or 411.3.2.3. 

Uo 
is the nominal a.c. or d.c. line to earth voltage in volts (V).

NOTE Where compliance with this subclause is provided by an RCD, the disconnecting times in accordance with Table 41.1 relate to prospective residual fault currents significantly higher than the rated residual operating current of the RCD (typically 5 I∆n). 

